## IS - 13980 original
Inputs
Output to be calculated based on formula
Bioler Efficiency Calculation By Heat Loss Method Unit (IS - 13980)
| DATE |  |  |  | Calculation
Symbol
Proximate Analysis - As fired | Ash | A | % | 1.914 | From Lab
| Volatile matter | VM | % | 1.8771 | From Lab
| Moisture | M | % | 50.5 | From Lab
| Fixed Carbon | FC | % | 45.7089 | From Lab
| Sucrose |  | % | 2.34 | From Lab
| Gross Calorific Value | GCV | % | 2248.92 | From Lab
Ultimate Analysis - As fired | Sulphur | S | % | 0 | Lab value
| Carbon | C | % | 34.7983 | (fixed Carbon (From Lab)) + 0.9 * (Volatile Matter(From Lab) - 14)
| Hydrogen | H | % | 1.1372 | (Volatile Matter (From Lab)) * (7.35/((Volatile Matter (From Lab)+10) - 0.013)
| Nitrogen | N | % | 2.0775 | (2.1 - (0.012*(Volatile Matter (From Lab)))
| Oxygen | O | % | 9.573 | 100-Carbon-Hydrogen-Nitrogen-Sulphur-Ash From Lab - Moisture From Lab
Boiler Parameters | Avg Flue Gas O/L Temp | T | OC | 182.83 | Boiler Air Pre Heater out let Temp
| Ambient Temp (Dry bulb) |  | OC | 26 | From Lab Ambient Temp (Dry bulb)
| Ambient Temp (Wet Bulb) |  | OC | 18 | From LabAmbient Temp (Wet Bulb)
| Ambient Temp (Dry bulb + Wet bulb)/2 | t | OC | 22 | From Lab Ambient Temp (Dry bulb) + From LabAmbient Temp (Wet Bulb) /2
| O2 at APH Inlet | O2 | % | 8.97 | Boiler Air Pre Heater In let O2 %
| CO2 at APH inlet | CO2 | % | 11.7649 | Boiler Air Pre Heater In let CO2 %
| CO at APH inlet | CO | % | 0.0651 | Boiler Air Pre Heater In let CO %
| N2 at APH inlet | N2 | % | 79.2 | Boiler Air Pre Heater In let N2 %
| Boiler Load | kg/h |  | 32000 | Boiler Load kg/h (Fix)
| Evaporation Ratio |  |  | 2 | Evaporation Ratio (Fix)
| Bagasse Consumption | kg/h |  | 16000 | (Boiler Load kg/h (Fix)) / (Evaporation Ratio (Fix))
| Quantity of atomizing steam | kg/h | Wze | 0 | From Lab
LOI | Unburnts in bottom ash | UBA | % | 84.7837 | From Lab
| Unburnts in Fly ash | UFA | % | 78.8446 | From Lab
Efficiency Tabulation (Heat Loss Method ) | Loss due to Unburned carbon | Luc | kcal/kg | 2.386 | kg of total dry refuse per kg of AF fuel * HHV of total dry refuse
| kg of total dry refuse per kg of AF fuel | Wd'p' | kg/kg | 0.01914 | Weight of dry refuse collected / Measured fuel rate
| Weight of dry refuse collected | Wd'p'e | kg/h | 306.2422 | Bagasse Consumption * ASH From Lab / 100
| Measured fuel rate | Wfe | kg/h | 16000 | Bagasse Consumption
| HHV of total dry refuse | Hd'p' | kcal/kg | 124.6596 | (70/100 * ASH From Lab / 100 * Unburnts in Fly ash / 100 * 8078) + (ASH From Lab / 100 * 30 / 100 * Unburnts in bottom ash / 100 * 8078)
| Loss due to Dry flue gas | Lg | kcal/kg | 287.3383 | Weight of dry gas leaving unit per kg of AF fuel * Mean Sp. Heat of dyr Flue Gas * (Avg Flue Gas O/L Temp - Ambient Temp (Dry bulb + Wet bulb)/2)
| kg of carbon burnt per kg of AF fuel | Cb | kg/kg | 0.34769 | Carbon / 100 - (kg of total dry refuse per kg of AF fuel * HHV of total dry refuse / 8078)
| Weight of dry gas leaving unit per kg of AF fuel | WG' | kg/kg | 7.4046 | ((44.01* CO2 at APH inlet + 32 * O2 at APH Inlet + 28.02 * N2 at APH inlet +28.01 * CO at APH inlet ) / (12.01 * (CO2 at APH inlet + CO at APH inlet))) * (kg of carbon burnt per kg of AF fuel + Sulphur / 267)
| Mean Sp. Heat of dyr Flue Gas | CpG' | kcal/kg0C | 0.24128 | 1.01/4.186
| Loss due to moisture in fuel | Lmf | kcal/kg | 342.9327 | kg of moisture/kg of AF fuel * (Vapour Enthalpy at 0.07kgf/cm2 at APH o/l - Enthalpy of saturated liquid at t)
| kg of moisture/kg of AF fuel | mf | kg/kg | 0.505 | Moisture From Lab/100
| Vapour Enthalpy at 0.07kgf/cm2 at APH o/l | Wfe | kcal/kg | 679.5796 | (2501+(1.88*Temp at APH O/L))/ 4.186
| Enthalpy of saturated liquid at t | HRw | kcal/kg | 0.505 | kg of moisture/kg of AF fuel
| Loss due to moisture in Hydrogen | Lh | kcal/kg | 69.0093 | 8.936 * Hydrogen / 100 * (Vapour Enthalpy at 0.07kgf/cm2 at APH o/l - Enthalpy of saturated liquid at t)
| Loss due to atomizing steam | Lz | kcal/kg | 0 | Quantity of atomizing steam * (Vapour Enthalpy at 0.07kgf/cm2 at APH o/l - Enthalpy of saturated liquid at t ) / Bagasse Consumption
| Loss due to formation of CO | Lco | kcal/kg | 10.7987 | (CO at APH inlet / (CO2 at APH inlet + CO at APH inlet ) * 5644 * kg of carbon burnt per kg of AF fuel)
| Loss due to unburned hydrogen | Luh | kcal/kg | 0 | 0 Value
| Loss due to Unburned Hydrocarbons | Luhc | kcal/kg | 0 | 0 Value
| Loss due to radiation & convection | Lβ | kcal/kg | 33.7338 | 1.5 * Gross Calorific Value / 100
| Total Loss kcal/kg |  | kcal/kg | 712.4651 | Loss due to Unburned carbon + Loss due to Dry flue gas + Loss due to moisture in fuel + Loss due to moisture in Hydrogen + Loss due to atomizing steam + Loss due to formation of CO + Loss due to unburned hydrogen + Loss due to Unburned Hydrocarbons
| Total Loss % |  | % | 31.6803 | Total Loss kcal/kg / Gross Calorific Value *100
| Boiler Efficiency | ηboiler | % | 68.3197 | 100 - Total Loss %